## Deterioration Modelling
Deterioration Modelling for Pressure Pipelines
Average Deterioration Rates (mm/year)
Water | 0.2344
Wastewater | 0.3462
Stormwater | 0.2344
[5 empty] | Data Required for Deterioration Modelling | [6 empty] | Variables |  |  | Results
Sample # | DN | Class | Use | Location / Address / Notes | Year Installed | Year Recovered | Operating Pressure (m) | Mean Pipe OD (mm) | Min Wall Thickness (mm) | Max. Ext Det'n | Max. Int Det'n | MPa | Surge Factor | National Det'n Rate | Sample Det'n Rate | Comparison to Nat. Avg. | Estimate Pipe Life | Est. Year of First Det'n Failure
Example 1 | 100 | CD | Water | Site 1 | 1958 | 2016 | 65 | 126 | 14.7 | 2.9 | 8.2 | 15.5 | 1.5 | 0.2344 | 0.19138 | 18% Slower | 57.1461 | 2015.1461
Example 2 | 150 | CD | Water | Site 2 | 1984 | 2016 | 42 | 179.7 | 15.8 | 3.7 | 4.8 | 23.5 | 1.5 | 0.2344 | 0.26562 | 13% Faster | 50.7204 | 2034.7204
Example 3 | 200 | CD | Water | Site 3 | 1963 | 2016 | 61 | 234.5 | 19.6 | 4.3 | 7.2 | 22.1 | 1.5 | 0.2344 | 0.21698 | 7% Slower | 68.8647 | 2031.8647
Example 4 | 100 | D | Wastewater | Site 4 | 1954 | 2016 | 15 | 130.1 | 20.1 | 6.2 | 11.3 | 15.5 | 1.5 | 0.3462 | 0.28226 | 18% Slower | 67.9597 | 2021.9597
Example 5 | 225 | B | Wastewater | Site 5 | 1962 | 2016 | 6 | 262.8 | 16.5 | 3.5 | 6.4 | 22.1 | 1.5 | 0.3462 | 0.18333 | 47% Slower | 87.1485 | 2049.1485
Example 6 | 375 | B | Wastewater | Site 6 | 1987 | 2016 | 50 | 417.4 | 23.5 | 4.1 | 5.7 | 23.5 | 1.5 | 0.3462 | 0.33793 | 2% Slower | 50.5434 | 2037.5434

## Constants
Deterioration Modelling - Lookup Data / Default Values
Gravity (m/s2) | 9.789
Surge Factor | 1.5
Material MPa Ratings by Year
Start Year | MPa Rating
0 | 15.5
1959 | 22.1
1976 | 23.5