## Slide 1
ASSESSMENT AND ACCEPTANCE OF NEW STORMWATER PIPELINES
Husham Issa Al-Saleem (Free Lance Consultant), Steve Apeldoorn (ProjectMax)

## Slide 2
New Stormwater System Construction: Main Objective
To convey stormwater from certain catchment to discharge it to the sea, natural watercourse or a structure leading to the sea or natural watercourse.
  Network pipes discharge capacity
  Grade
  Pipe size
  Connections and structures
  Materials
  Specified Quality Requirements to assure complying with the functional requirements set during the investigation and design stages of the project.

## Slide 3
Most NZ Territorial Authorities specify that newly installed Stormwater pipelines shall be constructed to a quality that meets their objectives (free from defects) before accepting their ownership.
Most new specifications nominate CCTV inspection as per the New Zealand Pipe Inspection Manual (NZPIM) as the acceptable method to assure quality of the newly installed Stormwater pipelines.
The NZPIM condition grading methodology has been designed to evaluate existing assets for maintenance and renewal planning, and not determining which individual pipes require repair or the acceptance of new pipe.
The draft of the new fourth Edition of the NZPIM, which is more specifically renamed as New Zealand Gravity Pipe Inspection Manual (NZGPIM) sets out to resolve this by including a new section specifically for inspection and assessment of defects in newly constructed assets.
Quality Requirements

## Slide 4
NZGPIM assessment criteria provides a new section specifically for inspection and assessment of defects in newly constructed assets:
  Based on typically acceptable industry practices and standards.
  Site specific and local requirements are left to be verified by Engineering Assessment on case by case bases.
  Presents a proposed procedure for the industry to follow though the inspection and acceptance process.
  Deals with acceptance as a pure engineering process, and it is up to the Engineer, not the “Inspecting Technician” to analyse the CCTV inspection footages and recommend future steps.
New Zealand Gravity Pipe Inspection Manual (NZGPIM)

## Slide 5
When the New Zealand Gravity Pipe Inspection Manual (NZGPIM) is published and adopted by NZ Authorities, assessment and acceptance of new Stormwater Pipelines is proposed to be done typically based on the following requirements wherever applicable, in the following order of precedence:
  1. Project Specifications and drawings
  2. Asset Owner’s Codes of Practice
  3. New Zealand Gravity Pipe Inspection Manual
  4. Pipe manufacturer’s recommendations, manuals, and trade associations literature
  5. International Specifications, research work and case studies.
  6. Engineering Experience.
New Zealand Gravity Pipe Inspection Manual (NZGPIM)

## Slide 6
New Pipelines Quality Objectives
  1. Not adversely affect the environment by:
  • Causing flooding
  • Contaminating or damaging receiving watercourses
  • Contaminating groundwater
  • Causing odors or producing corrosive gases.
  Structural integrity under design loads
  Durability to achieve design life
  Water tightness to specified level
  Ability to be maintained as planned
  Does not adversely affect adjacent soil, structures and utility services
  Maintaining design flow.

## Slide 7
Available Testing and Assessment Methods
Hydrostatic test
Air pressure test
INVASIVE AND DESTRUCTIVE TESTING
CCTV INSPECTION
laser profiling or proving pigs

## Slide 8
CCTV inspection and Assessments
  Preliminary CCTV Operator’s Observations and Logs
All manufacturing marks, stamps, writing, scratches or stains appearing on the pipe surface
The location, position and full longitudinal or circumferential extent of the pipe
Chipping or spalling of crack edges and whether it is a single or branching crack
Signs of autogenous healing
Evidence of infiltration
Any signs of exposed reinforcement or corrosion
Joint gap opening or angular deflection
Joint displacements
Exposed joint seals and seal locations
Ovality/deflection of the pipe
Dimples, bulges and other reflective shapes in close fit liners

## Slide 9
  2. Preliminary Assessment
Defect | Description | More Conditions | Acceptable | Engineering Assessment | Repair or Replace
Longitudinal Crack | Less than 300mm long |  | ü |  | 
 | Autogenously healed |  | ü |  | 
 | Less than 0.15mm width | Full pipe section (joint to joint) | ü |  | 
 | 0.15mm-0.5mm | Full pipe section (joint to joint)1 |  | ü | 
 |  | Full pipe section & observed in more than one quadrant1 |  | ü | 
Longitudinal Crack | 0.5mm-1.0mm | Full pipe section (joint to joint)1 |  | ü | 
 |  | Full pipe section & observed in more than one quadrant |  |  | ü
 |  | In an aggressive environment |  |  | ü
 | More than 1.0mm |  |  |  | ü

## Slide 10
  3. Collection Of Relevant Information For Engineering Assessment (Minimum Requirements)
Hydraulic and structural design data, parameters or assumptions
Plans and long sections of the installation to verify location and effect on other structures.
Geotechnical and chemical tests of surrounding soil
Test results on bedding materials and compaction results
Understanding of the embedment material compaction methods and equipment
Any notes in drain layer logs or pipes delivery sheets regarding factory repairs or pre-installation defects.
Any notes or information on post-installation repairs if any.
Dates and conditions of installation
Measurement of pipe gradient and any variation of gradient
Existence of dips where self-flushing gradients might not occur

## Slide 11
  Engineering Assessment
    Structural Stability: Evaluate the effect of each defect on the structural stability of the pipeline based on previous knowledge both in New Zealand and overseas, and the site-specific conditions of pipe location and installation methods.
    Durability: Predict compliance of the installation with this requirement from CCTV observations, site-specific conditions, and other background information to evaluate the effects on achieving the design life.
    Water and Silt tightness: Evaluate pipe water and silt tightness based on direct observation, CCTV date of investigation, site-specific conditions, and other background information as mentioned above.
    Hydraulic Capacity: Evaluate defects that might affect the required hydraulic capacity of the pipeline.

## Slide 13
If the Engineering assessment includes items where compliance is not a clear, final decision on what action required might be based on the following:
Review of design assumptions such as loading and hydraulic capacity
Cost value decision of the contractor if the cost of repair or replacement justify more spending on further investigation.
Asset Owner’s acceptance or compensation arrangement for future risk.

## Slide 14
Case Study
The CCTV Log sheets highlighted the following defects:
79 Joint Failure including chipping or longitudinal cracks in the joint zone
73 Circumferential Cracking of various severity
35 Open Joints
19 Longitudinal Cracks
7 Permanent Obstructions
5 Displaced Joints
4 Surface Damage
4 Multiple Cracks.

## Slide 15
Case Study
  Engineering Assessment
Defects assessed by CCTV inspector as “joint Failure” are:(Example of the assessment)
  Alternatively, short shrinkage cracks in pipe collars that frequently happened during manufacturing of concrete pipes due to reinforcement placement in the pipe as per Figure (1) which increase the thickness of cover, and hence, make concrete prone to shrinkage cracking.
All Circumferential Cracks were less than 0.25mm width, free from any signs of excessive infiltration and had clear signs of Autogenous healing. Having no threat to structural stability of the pipes because the pipes are designed as continuous ring structures and CC cracks of any width has no structural significance. Crack width, and installation information indicated that there was no chance of soil migration through any of them.

## Slide 16
Main Conclusions
The assessment of CCTV inspections of new stormwater pipe installation is a completely different process from that of the condition assessment of existing pipelines using the scoring analysis process in the NZPIM. The new pipeline assessment is a QA process that is intended to assure asset owners that the new assets meets their design, specifications and quality objectives.
Engineering assessment might require a review of various design and installation processes, design and properties of the installed pipes, verification of the pipeline service conditions, geotechnical information, quantitative pipeline testing and other relevant data to verify compliance.
The new draft version of the NZ Gravity Pipe Inspection Manual includes for the first time a special section on assessment of new pipelines. The Draft of the manual includes verification procedure and guidelines which are designed to facilitate preliminary assessment of the CCTV inspection and verification of which defect might need Engineering assessment.