## Slide 1: TMCo CRUSHED GLASS PRESENTATION A SUITABLE ALTERNATIVE TO 2A SAND?
STRUCTURAL | MECHANICAL | CIVIL | HYDRAULIC | ELECTRICAL | FIRE | ENERGY

## Slide 2
Marc Jensen – TM Consultants Limited
Equity Associate (shareholder), Senior Mechanical and Hydraulics Engineer
BEngTech (Mech), NatDip (Mech), Dip (Mech)
Corresponding Author for the Crushed Glass As A Filter Medium For On-site Wastewater Treatment conference paper.
Committee Member OWMS (SIG) WaterNZ
Chair of EPAC Engineering Advisory Group
OWMS Working Group – Committee Member
Accredited Site and Soil Evaluator
Certified Lifestyle Service Technician
Suitably Qualified and Experienced Person (OSET)
Designed 350+ NZ, Chatham Islands and International onsite wastewater treatment plants
Passionate sustainability advocate, photographer and fisherman
INTRODUCTION

## Slide 3
It is estimated that around 270,000 homes in New Zealand rely on onsite wastewater management systems (OWMS).
2A sand has been used as a filter medium for a long time and has a good track record.
At present, almost all recycled glass in New Zealand end up in landfills; 60,000 tons in 2016.
Meanwhile, 2A sand must be quarried from selected rivers dispersed across the country.
INTRODUCTION
Notes: Southland data - Ministry for the Environment, "Proposed National Environment Standard for On-site Wastewater Systems," July 2008. [Online].

## Slide 4
It is estimated that around 270,000 homes in New Zealand rely on onsite wastewater management systems (OWMS) to manage their wastewater.
  Approximately 75 per cent of homes in Southland are not reticulated and use an OWMS.
2A sand has been used as a filter medium for a long time and has a good track record.
  2A sand can remove up to 98% of Biochemical Oxygen Demand (BOD5),
  94% of Total Suspended Solids (TSS),
  27% of Total Nitrogen (TN) and a
  log 3 of Faecal Coliform (FC) in the septic tank effluent from a single home.
At present, almost all recycled glass in New Zealand end up in landfills; 60,000 tons in 2016,
With a fraction being used as aggregates, sandblasting media, or landscaping materials,
Meanwhile, 2A sand must be quarried from selected rivers dispersed across the country.
Can recycled glass, once crushed, be used to treat effluent?
INTRODUCTION
Can recycled glass, once crushed, be used to treat effluent?
Notes: Southland data - Ministry for the Environment, "Proposed National Environment Standard for On-site Wastewater Systems," July 2008. [Online].

## Slide 5
Southland Population per 1km2
  Approximately 75 per cent of homes in Southland are not reticulated and use an OWMS.
Notes: Southland data from - Ministry for the Environment, "Proposed National Environment Standard for On-site Wastewater Systems," July 2008. [Online].

## Slide 6
How about Taranaki?

## Slide 7
TM Consultants, ARA Institute of Technology and a final year Civil Engineering Student created a project to evaluate the performance of Crushed Glass (CG) with respect to 2A sand when treating primary treated effluent.
A test rig was designed and constructed to simulate the environment of the sand column in a discharge control trench.
The treatment efficiency of three filters was recorded and compared in this study.
As a control, 2A sand was loaded at 50mm/day.
Crushed glass was loaded at both 25mm/day and 50mm/day.
PROJECT BRIEF

## Slide 8
METHODOLOGY AND TEST RIG
Notes: Have you ever cold called someone and asked if you can take samples of what they flush down the toilet? Well me neither. I asked the student to do it!
He was a legend and found a family in Wainui, and collected samples rain or shine with a 20Ltr container. And kept the test rig topped up for 17 weeks.
It was noted that the family providing effluent samples were advised to not change their existing cleaning regime, chemicals and to continue using the system as per their normal. To not throw off the testing.
CG 50 and 25 mm/m2/d. Hence the two different pipe diameters.
The filters were dosed three times per day to mimic domestic loading.
Highest load in the morning, light at lunch, medium loading at night. A rest period of eight hours between pumping cycles.
The test rig was located in an airconditioned laboratory at ARA at the Madras Street Campus.
average temperature 19°C

## Slide 9
ACTUAL SAMPLES
Notes: CG, obtained from Fulton Hogan Quarries Canterbury
Crushed glass isn’t washed and still has labels etc.

## Slide 10
ACTUAL SAMPLES
Notes: From the bed of braided rivers such as
Can cause excess sediment to flow downstream and damage sensitive habitats for native fish species etc.

## Slide 11
SAMPLE GRADING – 2A MESO DIAGRAM
Notes: Both samples however were both met the 2A grading.

## Slide 12
HOW CLEAN?
2A Sand is washed when produced, this leads to relatively clean effluent on the first day.
Crushed glass is not currently washed when produced.
Residual wine, beer or other residues that remain in the bottles at the time of crushing lead to dirty effluent with a higher TSS than the influent.
Higher loading rates flush the crushed glass quicker than lower loading rates.
By the 146th day, all samples appeared identical (clear) to a visual inspection.
TMCo recommend that all crushed glass substituting 2A sand in effluent systems is washed prior to installation. (Potential resource consent condition?)

## Slide 13
CONTROL – 2A SAND COLUMN

## Slide 14
TOTAL SUSPENDED SOLIDS
The removal of TSS and BOD5 in wastewater is accomplished by both physical and biological mechanisms.
The filter media acts as a strainer (infiltration and percolation) to retain solids from wastewater and the naturally occurring microbes inside the filter will consume contaminants and eventually form a microbial biomat.
A healthy biomat can remove bacteria and viruses.
A working filter with abundant oxygen and food supply (contaminants in wastewater) should exhibit a consistent reduction of TSS and BOD5 once established (after week 5 in our testing).

## Slide 15
TOTAL SUSPENDED SOLIDS – KEY FINDINGS
There were a few special occasions that resulted in the abnormally high concentration of TSS and BOD5.
Week 11 to week 13 - lockdown
Week 17 - long weekend of Labor Day (extra load).
The CG50 filter showed a slightly fluctuating trend over the first seven-week period then achieved a 100% removal rate for most of the weeks after.
The CG25 filter showed the lowest removal rate in the three over the first seven-week period.
Chart: TSS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Septic tank | 40 | 72.5 | 77.5 | 55 | 40 | 70 | 50 | 40 | 40 | 60 | 67.5 | 72.5 | 50 | 50 | 40 | 50 | 77.5
Sand Filter (50mm FL) | 10 | 0 | 2.5 | 2.5 | 5 | 10 | 0 | 0 | 0 | 0 | 7.5 | 2.5 | 0 | 0 | 0 | 0 | 7.5
CG Filter (50mm FL) | 320 | 7.5 | 10 | 7.5 | 0 | 10 | 5 | 0 | 0 | 0 | 7.5 | 2.5 | 0 | 0 | 0 | 0 | 7.5
CG Filter (25mm FL) | 470 | 17.5 | 7.5 | 15 | 5 | 10 | 5 | 0 | 0 | 0 | 7.5 | 2.5 | 0 | 0 | 0 | 0 | 7.5
Sand Filter Efficiency (50mm FL) | 75 | 100 | 96.7742 | 95.4545 | 87.5 | 85.7143 | 100 | 100 | 100 | 100 | 88.8889 | 96.5517 | 100 | 100 | 100 | 100 | 90.3226
CG Filter Efficiency (50mm FL) | 89.6552 | 87.0968 | 86.3636 | 100 | 85.7143 | 90 | 100 | 100 | 100 | 88.8889 | 96.5517 | 100 | 100 | 100 | 100 | 90.3226
CG Filter Efficiency (50mm FL) | 75.8621 | 90.3226 | 72.7273 | 87.5 | 85.7143 | 90 | 100 | 100 | 100 | 88.8889 | 96.5517 | 100 | 100 | 100 | 100 | 90.3226
Filter Loading (FL) reported as L/m2/day | 1

## Slide 16
Chart: TSS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Septic tank | 40 | 72.5 | 77.5 | 55 | 40 | 70 | 50 | 40 | 40 | 60 | 67.5 | 72.5 | 50 | 50 | 40 | 50 | 77.5
Sand Filter (50mm FL) | 10 | 0 | 2.5 | 2.5 | 5 | 10 | 0 | 0 | 0 | 0 | 7.5 | 2.5 | 0 | 0 | 0 | 0 | 7.5
CG Filter (50mm FL) | 320 | 7.5 | 10 | 7.5 | 0 | 10 | 5 | 0 | 0 | 0 | 7.5 | 2.5 | 0 | 0 | 0 | 0 | 7.5
CG Filter (25mm FL) | 470 | 17.5 | 7.5 | 15 | 5 | 10 | 5 | 0 | 0 | 0 | 7.5 | 2.5 | 0 | 0 | 0 | 0 | 7.5
Sand Filter Efficiency (50mm FL) | 75 | 100 | 96.7742 | 95.4545 | 87.5 | 85.7143 | 100 | 100 | 100 | 100 | 88.8889 | 96.5517 | 100 | 100 | 100 | 100 | 90.3226
CG Filter Efficiency (50mm FL) | 89.6552 | 87.0968 | 86.3636 | 100 | 85.7143 | 90 | 100 | 100 | 100 | 88.8889 | 96.5517 | 100 | 100 | 100 | 100 | 90.3226
CG Filter Efficiency (50mm FL) | 75.8621 | 90.3226 | 72.7273 | 87.5 | 85.7143 | 90 | 100 | 100 | 100 | 88.8889 | 96.5517 | 100 | 100 | 100 | 100 | 90.3226
Filter Loading (FL) reported as L/m2/day | 1

## Slide 17
The sand filter showed a good and consistent performance with a gradual increase in the BOD5 removal rate over the seventeen weeks.
Week 3 - 7 and week 12 - 15, the sand filter achieved a 95.9% removal which coincided with the times when the filter achieved a 100% removal rate TSS.
The CG50 filter showed a slightly fluctuating curve at the start of the trial, from week one to week five, but gained a steady increase in the BOD5 removal rate afterwards, averaging nearly 95.1% reduction from week 10 - 15.
The CG25 filter showed lower BOD5 removal rates in weeks 2 - 4 but performed better from week 5 forward to the end of the period.
In general, each filter seemed to have a different removal efficiency at the start, but all of them got to their maximum removal rates after week 6 in excess of 95%.
BOD5 – KEY FINDINGS
Chart: BOD5
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Septic tank | 41.8 | 63.3 | 117.5 | 100.6 | 87.1 | 141.6 | 83.2 | 59.2 | 69 | 81.4 | 161.1 | 167.985 | 152.805 | 114.9 | 98.8 | 84.8 | 128.4
Sand Filter (50mm FL) | 0.1 | 7.5 | 12.4 | 7.2 | 6.7 | 6.3 | 3 | 0.8 | 3.6 | 2.8 | 14.8 | 5.535 | 2.655 | 3.3 | 1.9 | 1.4 | 4.8
CG Filter (50mm FL) | 120.4 | 5.1 | 8.2 | 10.1 | 9.7 | 8.1 | 5.6 | 1.9 | 2.4 | 5.2 | 5.5 | 2.985 | 4.005 | 5.1 | 3.4 | 2 | 5.1
CG Filter (25m FL) | 221.2 | 19.8 | 29.3 | 8.8 | 7.3 | 7.8 | 4 | 1.3 | 2.7 | 2.8 | 12.9 | 10.185 | 6.405 | 6.6 | 4.3 | 2.6 | 6.3
Sand Filter Efficiency (50mm FL) | 88.1517 | 89.4468 | 92.8429 | 92.3077 | 95.5508 | 96.3942 | 98.6486 | 94.7826 | 96.5602 | 90.8132 | 96.7051 | 98.2625 | 97.1279 | 98.0769 | 98.3491 | 96.2617
CG Filter Efficiency (50mm FL) | 91.9431 | 93.0213 | 89.9602 | 88.8634 | 94.2797 | 93.2692 | 96.7905 | 96.5217 | 93.6118 | 96.586 | 98.2231 | 97.379 | 95.5614 | 96.5587 | 97.6415 | 96.028
CG Filter Efficiency (25mm FL) | 68.7204 | 75.0638 | 91.2525 | 91.6188 | 94.4915 | 95.1923 | 97.8041 | 96.087 | 96.5602 | 91.9926 | 93.937 | 95.8084 | 94.2559 | 95.6478 | 96.934 | 95.0935
Filter Loading (FL) reported as L/m2/day | 1
Notes: One COVID-19 lockdown resulted in increased occupancies over three weeks during testing.

## Slide 18
Chart: BOD5
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Septic tank | 41.8 | 63.3 | 117.5 | 100.6 | 87.1 | 141.6 | 83.2 | 59.2 | 69 | 81.4 | 161.1 | 167.985 | 152.805 | 114.9 | 98.8 | 84.8 | 128.4
Sand Filter (50mm FL) | 0.1 | 7.5 | 12.4 | 7.2 | 6.7 | 6.3 | 3 | 0.8 | 3.6 | 2.8 | 14.8 | 5.535 | 2.655 | 3.3 | 1.9 | 1.4 | 4.8
CG Filter (50mm FL) | 120.4 | 5.1 | 8.2 | 10.1 | 9.7 | 8.1 | 5.6 | 1.9 | 2.4 | 5.2 | 5.5 | 2.985 | 4.005 | 5.1 | 3.4 | 2 | 5.1
CG Filter (25m FL) | 221.2 | 19.8 | 29.3 | 8.8 | 7.3 | 7.8 | 4 | 1.3 | 2.7 | 2.8 | 12.9 | 10.185 | 6.405 | 6.6 | 4.3 | 2.6 | 6.3
Sand Filter Efficiency (50mm FL) | 88.1517 | 89.4468 | 92.8429 | 92.3077 | 95.5508 | 96.3942 | 98.6486 | 94.7826 | 96.5602 | 90.8132 | 96.7051 | 98.2625 | 97.1279 | 98.0769 | 98.3491 | 96.2617
CG Filter Efficiency (50mm FL) | 91.9431 | 93.0213 | 89.9602 | 88.8634 | 94.2797 | 93.2692 | 96.7905 | 96.5217 | 93.6118 | 96.586 | 98.2231 | 97.379 | 95.5614 | 96.5587 | 97.6415 | 96.028
CG Filter Efficiency (25mm FL) | 68.7204 | 75.0638 | 91.2525 | 91.6188 | 94.4915 | 95.1923 | 97.8041 | 96.087 | 96.5602 | 91.9926 | 93.937 | 95.8084 | 94.2559 | 95.6478 | 96.934 | 95.0935
Filter Loading (FL) reported as L/m2/day | 1

## Slide 19
BOD5 AND TSS – KEY FINDINGS
Effluent out the base of the sand columns all met or exceeded the requirement for secondary treatment:
  BOD5: <20g/m3 with no sample > 30g/m3
  TSS: 90 % of sample <30g/m3 with no sample > 45g/m3

## Slide 20
The reduction of TN relies on the conversion of Ammonia to Nitrite and from Nitrite to Nitrate through natural processes such as denitrifying bacteria and other mechanisms.
Tested for TN on week 16 -17 of the trial, all filters achieved removal rates within the 55% to 70% range as shown in Table 2.
The two CG filters had similar removal rates, and both were better than the sand filter.
Additional nitrate reduction testing is required and is proposed to be completed in 2023.
TN – KEY FINDINGS

## Slide 21
AVERAGE REMOVAL RATES

## Slide 22
CG could be a suitable substitute for 2A sand.
Suitable for loading rates up to 50mm/day.
Overall, when having the same hydraulic loading, CG performed similarly to 2A sand in terms of TSS, BOD5 reduction.
CG achieved a higher TN reduction than 2A sand.
After eight weeks, loading rates had little effect on the performance of both filters with both achieving similar levels of treatment.
CONCLUSION - TREATMENT

## Slide 23
The price of CG was half of 2A sand (before latest price hikes),
Produces significantly less CO2 emissions than 2A sand to produce,
CG when used as filter media for a 3-bedroom dwelling could save up to $500 and reduce 200 kg of CO2 released to the environment.
The case study for a mobile glass crusher shows that investing in a mobile glass crushing unit could be beneficial.
It will only take 2.4 years for the operation to return $134,000 capital to the investors and after that, the price of CG could be reduced significantly from $26 to $15/m3.
Using crushed glass as a filter medium could lower the material cost for a trench filter and potentially create a viable market for the abundant recycled glass stockpile in New Zealand.
CONCLUSION – SUSTAINABILITY AND COST

## Slide 24
This project would not have been possible without these key individuals.
ARA Institute of Technology for hosting the final year project.
Quang Truong (ARA student) who built, iterated and operated the test rig.
Dr Matt Pour (ARA) for supervising the project and assisting in the publishing of the technical paper.
Mike Baker (TM Consultants) for his continued support and encouragement.
Issei Yuki (TM Consultants) for checking and reviewing posters, papers and calculations.
Ashley Watson (TM Consultants) for reviewing posters and test rig results.
THANKS

## Slide 25
Any Questions?
Thanks for Listening

## Slide 26
Septic Systems Australia, “Secondary Treatment: Septic Tank with Sand Filter and Subsurface Irrigation,” December 2017. [Online]. Available: https://www.septicsystemsaustralia.com.au/septic-tanks-sand-filter. [Accessed 10 August 2021].
Clean Washington Center, “Crushed Glass as a Filter Medium for the Onsite Treatment of Wastewater,” Mar-1997. [Online]. Available: http://www.loveyourhottub.com/content/vitroclean-evaluation-for-wastewater.pdf. [Accessed: 17-Mar-2021].
J. Webber, A. Slack and P. Chrystall, “Glass Recycling Options in New Zealand,” 31 January 2009. [Online]. Available: https://www.wasteminz.org.nz/wp-content/uploads/GLASS-RECYCLING.ppt. [Accessed 12 August 2021].
L. Gill, C. Doran, D. Misstear and B. Sheahan, “The use of recycled glass as a filter media for on-site wastewater treatment,” Desalination and Water Treatment, vol. 4, no. 1, pp. 198-205, 2008.
A. Selvakumar, M. Borst, M. Boner and P. Mallon, “Effects of sample holding time on concentrations of microorganisms in water sample,” Water Environment Research, vol. 1, pp. 67-72, 2004.
REFERENCES