## Slide 1
Hayden Pipe (Stantec) and Todd Randell (Hynds)
18 October 2022
Kaitoke Flume Bridge Replacement: Using Seismic Resilient Ductile Iron Pipe
Notes: Intro – Kia ora
Hayden
Todd – Business Development Manager
Hynds worked with us
Outline – Network/Existing Infrastructure/Level of service/Todd – SRDIP/Why we chose SRDIP/Modelling in seismic event
Photo early 1950s
Intro – Hayden and Todd
Kia ora. My name is Hayden Pipe, and I’m a Civil Engineer in the Three Waters Space at Stantec in Wellington and with me I have Todd Randell who is a Business Development Manager at Hynds Pipe Systems. His role includes finding unique specialist pipeline solutions for customers and asset owners. Hynds have worked with us, once the decision was made to use SRDIP, to help us achieve a successful solution for the Kaitoke Flume Bridge Replacement Project for our client, Wellington Water and the water users in the Greater Wellington Region..
Summary of presentation
As part of this presentation, we are going to:
Take you through how the Kaitoke Flume Bridge fits into the Wellington Drinking Water Supply network and its importance
What the original infrastructure consists of and why it needs replacing
What level of service the new structure will be designed to
I’ll then pass you over to Todd who will provide some detailed background on what SRDIP is and how it performs in a seismic event.
I’ll then jump back in and give some detail around why we chose SRDIP as our pipe material
And then finish on some detail on how our modelling predicts the pipe will perform in the design seismic events.
Just to finish off this slide, as a matter of interest, this photo was taken in the early 50s when the existing flume bridge was in construction.

## Slide 2: Wellington Region Bulk Network
Notes: Wellington Regional Bulk Network
Four extraction points
Te Mārua 40% plus
Fault line
Treatment Plant and Lakes – 3000 million litres. Use for project.
The Wellington Regional relies on four separate water extraction points. If we start from the bottom up, we have the combined flows form the Wainuiomata and Orongaronga rivers. We then have Gear Island and Waterloo which pump water from the Upper Waiwhetu aquifer. And finally there is Te Mārua, where water is conveyed from the Hutt River upstream, including over the Kaitoke Flume Bridge. Te Mārua supplies 40% of the Wellington Region’s supply each year – but at times will supply more depending on demand and the operation of other sources.
As a point of reference, the red line is the Wellington Fault line.
Te Mārua is a drinking water treatment plant but also contains the two large Macaskill Storage Lakes to supplement supply if required. These lakes hold a useable supply of about 3,000 million litres. We are using the lakes to help supply the Wellington Region when we need to shut off the Kaitoke Intake to make connections during construction.
Four Sources
Waterloo and Gear Island pumped aquifer supply
Wainuiomata & Orongaronga Rivers
Te Mārua fed from Hutt River via Kaitoke Flume Bridge. Te Mārua is a treatment plant but also contains two large Macaskill Storage Lakes to supplement supply if required.
Red line – Major Wellington Fault line as point of reference
The allowable take from the Hutt River upstream of the Kaitoke Flume Bridge is 150 MLD. Supplies 40% of Wellington’s supply each year – but at times will supply more depending on the demand and operations of other sources.

## Slide 3: Intake System
Notes: Intake System
Raw Water intake weir
Upper reaches
Tunnel
Flow control
Minimum river flow
Photos
The raw water for Te Mārua is extracted by gravity at the intake weir in the upper reaches of the Te Awa Kairangi or Hutt River. The river water then flows through a tunnel in the hill side and to the Kaitoke Flume Bridge. The flow is controlled by 2 intake valves which are throttled to ensure that a minimum river flow is achieved and that the capacity of the strainer house downstream of the bridge is not exceeded. The photo on the left shows the intake weir. You can see the rail irons on the upstream side of the weir, which the water flows through. The photo on the right is taken underneath the weir where flow control and scour equipment is located.

## Slide 4: Intake System
Notes: Intake System 2
Describe Gravel trap
Small amount of gravel
Don’t need to keep gravel trap
Keep for constructability reasons and abrasion
As just mentioned, on the downstream side of the tunnel, there is the existing bridge with a gravel trap just prior as shown in the left hand photo. This collects gravels prior to it going over the bridge. Only a small amount of gravel is collected as shown in this photo. The last time the gravel was cleared was 3 years before this photo was taken so it collects very slowly. For this reason, Wellington Water advised us that they did not have a preference either way if the gravel trap was removed as part of construction of the new bridge. However we did decide to keep it for both constructability reasons as it meant that a new connection to the tunnel portal was not required and it also helps minimise the abrasion the gravel would cause at the pipe invert.

## Slide 5: Existing Structure
Notes: Existing Structure
3 span flume box
Connections either side
2 concrete piers
Completed 1954
Strengthened 1992
Leaks, poor condition, seismic requirements
Critical structure
The existing Flume Bridge consists of a 3-span concrete flume box structure that connects to the gravel trap connecting to the tunnel portal on the northern (right) bank and a concrete pipeline on the southern (left) bank. It’s supported by two high concrete piers, located either side of the Te Awa Kairangi River. This bridge was completed in 1954 and strengthened in 1992. However it currently leaks, is in poor condition and does not meet seismic requirements. The structure is critical to Wellington’s Water supply and is therefore being replaced.

## Slide 6: Existing Structure
Notes: Existing Structure 2
Concrete pipeline poor condition
Leaks
Included in scope
The concrete pipeline downstream of the bridge, which also connects to a sand trap pictured in the foreground of the photo on the left is also in poor condition. It was built at the same time as the bridge and also leaks in multiple locations. This pipeline is also within the scope of works to be replaced with the extent of the works connecting to the sand trap.

## Slide 7: Seismic Design Requirements
Serviceability Limit State (SLS) Earthquake
Damage Control Limit State (DCLS) Earthquake
Collapse Avoidance Limit State (CALS)
Notes: Seismic Design Requirements
Waka Kotahi Bridge Manual – 100 year design life. DCLS with a return period of 1 in 1000 years and IL3 structural designiation.
Objectives
SLS. Remain in service – minimal damage to secondary elements
DCLS. Remain in service. Access compromised short term. Potentially significant damage. Repairable. Avoid collapse in repeat events. Relevelling or reseating of bridge may be required.
CALS. The big one. May not remain in service. Collapse prevented but extensive damage which will take some time to repair.
The new bridge and components were design to comply with the requirements of the Waka Kotahi Bridge Manual for a 100-year design life and a Damage Control Limit State Earthquake associated with a return period of 1 in 1000 years and IL3 structural designation. The seismic performance objectives are:
SLS (which is ######): Operational functionality of the pipe is maintained and there will be no damage to the primary structural elements, and minimal damage to secondary elements
DCLS (which is #####): Operational functionality of the pipe is maintained. Access might be compromised but is feasible to be recovered in 3 days. Structural damage might be significant but repairable to the extent sufficient to avoid collapse under a repeat event. Permanent differential displacement between the abutments and the bridge deck is acceptable, provided the bridge can be relevelled and re-seated.
CALS (which is #####): This is the big one where Operational functionality of the pipe compromised. Collapse is prevented but extensive damage to the structure is expected and will take some time to repair. A large permanent gap is expected between the abutments and the bridge deck.

## Slide 8: New Alignment
DN1500 pipeline
Built offline so bends required
Tower Crane Clash
Notes: Hydraulics
DN1500 pipeline.
Bends head losses
Gravel trap connection.
Temporary bend – crane.
Shutdown duration Macaskill lakes
Temp scenario will reduce capacity in the short term.
Downstream shallow tunnel and intake valve diameter – 135 MLD extra 25-30 MLD
- Hand over to Todd
The pipeline diameter chosen was DN1500. As you can see from this image, we have introduced a bend on the right hand end which will introduce head losses. There wasn’t much flexibility with the location of the abutment on the right hand side due to the geography so the connection to the gravel trap is slightly tighter than we would like. We have designed a rolled steel bend and minimised sudden changes in geometry in the gravel trap to help minimise losses at this connection whilst still allowing the gravel trap to operate as intended.
On the left side, you can see the pipeline going straight through as well as what is a temporary bend. The purpose of the temporary bend is to allow the pipe to be temporary commissioned whilst the tower crane is demolishing the existing bridge as the new pipeline. If we didn’t do this, the shutdown duration would be longer than the capacity in the Stuart Macaskill Storage lakes mentioned earlier. The additional bends in the temporary scenario is expected to reduce capacity of the pipeline from what the existing bridge can currently convey but this will not cause issues for Wellington Water in the short term. Once the bend is removed and the permeant solution is in place, this shortfall in the design capacity will no longer be an problem.
Overall, the main constriction of flow is a long, and very shallow, tunnel downstream of the bridge. Modelling shows the new pipeline will be able to convey approximately 134 MLD. This is similar to the existing flume. However there is a possibility in the future that with changes downstream and upstream or the bridge including finding a solution to push the water through the downstream tunnel and upgrading the size of one of the two intake valves to DN600, that the flow could be increased to approximately 162 MLD.
I’ll now hand you over to Todd to discuss the detail about the SRDI pipe.

## Slide 9: Water Pipeline Materials Selection
Material Selected:
SRDIP back-ground, was first invented in Japan 1974.
Survived many great earthquakes without joint leakage up to 9.0Mw.
Adopted by Japanese Water Works Association (JWWA) as the preferred DIP system.
9 joined-pipes DN600 (6.0m lengths) TYPE NS Mechanical SRDI Pipes lifted by crane showing radius of curvature. Source; JDPA

## Slide 10: Water Pipeline Materials Selection
Material Selected:
Type S Seismic Resilient Ductile Iron Pipe (SRDIP) manufactured by Kurimoto Ltd, Japan.
SRDIP provided:
    Excellent seismic resilience properties.
    Expansion and contraction at each joint +/- 60mm.
    Large allowable joint angular deflection.
    Good thermal properties.
    The highest resistance to pull out.
    Additional mechanical movement joints not required.
    Good rock fall and vandalism resistance.
Source: JDPA Japanese Ductile Iron Pipe Association

## Slide 11
Seismic resilient components
Expansion/contraction performance : ±1% of L
Slip-out resistance : 3d kN
Joint deflection angle : DN75～250) 8 degrees, DN300～450) 6 degrees, DN500～1000) 7 degrees & DN1500 5.8 degrees.
*L is the component length (mm), d is the nominal diameter of pipe (mm)
Expansion range
Contraction range
Special features of Type NS
SRDIP
2.Seismic Resilient Ductile Iron Pipe
Notes: NS形には３つの大きな特長があります。
There are 3 special features about Type NS.
１つ目は伸縮性であり、２つ目は離脱防止構造、3つ目は可撓性です。
The first is expansion contraction performance. The second is joint deflection angle. The third is slip-out resistance.
（図を挿しながら）挿し口から受口奥までが縮み代、挿し口突部からロックリングまでが伸び代です。
Contraction range is from the end face of the spigot to the back of the socket, and expansion range is from the projection part of spigot to the lock ring.
継手が限界まで伸びだすと、ロックリングと挿し口突部が掛かり合い離脱防止機能が働きます。
When the joint reaches maximum expansion range, the projection part is caught on the lock ring to active the slip-out resistance.

## Slide 12: SRDIP Joint Chain Link Structure
In Japan SRDIP is called “chain link structure”.
Example of a chain:
  Compressed.
  Extended.

## Slide 13
Special features of Type NS
SRDIP
2.Seismic Resilient Ductile Iron Pipe
Source: JDPA Japanese Ductile Iron Pipe Association
Notes: 実際に地震が発生した場合、継手は地中で動画のように動きます。
When an earthquake occur, Type-NS moves in the ground like this movie. ☆
地盤変動が一箇所に集中した場合、１つの継手が最大まで伸びると、その隣の管がのびます。
Cracks concentrate in one place.
After one joint expand to the maximum, the next joints starts to expand,
Type NS pipeline follows a ground movement.
加えて、このように可とう性があるため、地盤沈下にも対応します。
In addition, because of such flexibility, it follows a subsidence of a ground.

## Slide 14: Material Selection
Seismic Resilient Ductile Iron
Seismic Resilience – allowable joint movement
Thermal Expansion
Pull out force resistance
No mechanical movement joints required
Impact Resistance
Installation benefits – no welding
Notes: Spoiler alert:
60mm 5.83 degrees stresses/strains
Thermal
Pull out
Mechanical movement joints
Impact – rock fall
Quick joint installation – no welding. Cost and H&S benefits
So spoiler alert, we chose the SRDI pipe for this bridge. The main reasons for this were:
The obvious reason is the seismic resilient pipe joints which allow +/-60mm contraction and extensions at every joint. This obviously means that when the bridge or pipes need to move, this movement can be taken up within the pipe joints without putting large stresses or strains on the pipe barrel or joints.
The allowable movement in the joints also allows for thermal expansion so we do not need any thermal expansion joints along the pipeline.
The pipeline have large pullout force resistance.
No mechanical movement joints are required at each end of the bridge to allow for differential movement between the bridge and the land either side. At 1.5m diameter, this provide a very large cost saving.
The area has rock fall hazards, with the risks particularly high during a large earthquake. Some of the pipeline is exposed, particularly at the bridge ends where the risk is high so we felt it was reasonably important to have this attribute.
The joints are quick to make with no welding required. This has cost and health and safety benefits.

## Slide 15: Material Selection
Custom Steel Bends
Japanese Standard
Partially factory welded
Collars
Notes: Material Selection
Standard bend sizing
Don’t work with our rigid requirements. Fixed points
Steel specials required.
2 options
Transition piece – takes up room
Repair risks.
Benefits – more room for bend and cost.
Collar.
The SRDI pipes do have the usual standard bend sizes. However, for our project, these did not really fit with our rigid requirements where we have fixed points at either end to connect to and little room to make up any angles in the pipe joints. We therefore required steel specials to make our design work. We had 2 options in doing this. The first was to use NZ sized steel which has a different diameter to Japanese standard pipe sizings. This would have required a transition piece to connect the two. However any alternative was to use Steel Pipe imported from Japan. This would mean the transition pieces were not required and the steel pipe could be made to fit directly to the SRDI pipe. The downfall of this repairs may be more difficult in the future if steel pipe is required to make the repair. But the benefit of having more room to have a bend that was less sharp and the cost benefits outweighed the repair risk.
You may also note the double ended fitting between the gravel trap and bridge which is a SRDI collar. This is included in the design to join pipes and allow some differential movement between the gravel trap and the bridge abutment.

## Slide 16: Thrust Restraint
Minimal hydrostatic/hydrodynamic force
Potentially large seismic forces
Notes: Thrust Restraint
80% full
Minimal thrust
Large seismic force.
Pipe won’t stop
Isolate from other structures
The new pipeline will run about 80% full. This means that there will be minimal hydrostatic thrust forces to restrain. However we expect that there may be larger seismic forces. For a large event, The ground will accelerate and then stop. But as the pipes are sitting on low friction pads, the pipe may want to keep moving. We have therefore placed thrust restrain blocks at either end of the bridge to withstand these pulling or pushing forces and isolate it from structures either side of the bridge such as the sand trap or the gravel trap.

## Slide 17: Seismic Pipe Movement
Longitudinal movement – low friction pads
Transverse movement
Superstructure movement on abutments
Combinations of above
Notes: Seismic Pipe Movement
Longitudinal 11 joints for 150mm closer in CALS
Supports with polyethylene pads
Transverse. 230mm. Joints at end. 53m between ends means 0.25 degrees. Much less than 5.83 degrees.
Easily accommodate.
Further scenario more complex
There are a number of different ways the pipe can move in a large seismic event.
For Longitudinal movement in the CALS event, the north abutment is expected to move south 180mm and the south abutment is expected to move north 31mm. So this would result in the abutments moving 149mm closer. There are 11 pipe joints on the bridge with an allowance to expand or contract up to 660mm in total. Therefore, the joints can easily accommodate the worst case CALS scenario. The pipe supports have been designed to withstand the force induced by friction between the pipeline and the supports which have low friction polyethylene pads on the supports.
For Transverse movement: Modelling for the 100% CALS event results in the northern abutment moving 60mm in the northwest direction and the south abutment moving 170mm in the opposite direction resulting in 230mm differential transverse movement. This movement will need to be accommodated at the two pipe joints located at the very end of the bridge where the differential movement occurs between the bridge structure and the abutment. The pipeline length between the joints at each abutment is 53m. The 230mm differential transverse movement between abutments will result in a rotation of the joints at each abutment of 0.25 degrees which is well within the tolerance of the 5.83 degree allowable rotation at the SRDI pipe joints.
So as just described, the SRDI pipe can easily account for the longitudinal and transverse movements of the pipeline without putting significant stresses or strains on the pipe barrels or joints. However we have one further scenario which required a slightly more complex solution.

## Slide 18: Seismic Pipe Movement
Longitudinal movement
Transverse movement
Superstructure movement on abutments
Combinations of above
Notes: Seismic Pipe Movement
Access constraints – access bridges. Northern side
Pilling rig 600mm max not enough.
Holmes. Not fixed to the abutments. DCLS and CALS.
As you can see from this image, the bridge is located in a unique location with obvious access constraints. This has caused the team headaches with being able to get a piling rig large enough onto site, particularly to the northern side of the bridge which has no road access. And even though the left side of the bridge has road access, some of the bridges along the access road are not capable of large loads. The maximum pile diameter we could obtain in the hard rock is 600mm. We actually tested this prior to construction. At this diameter, the seismic forces would result in the piles failing during design events so another solution was required – which we came up with in conjunction with Holmes Consulting who undertook the structural design of the bridge structure. The final network arch superstructure design is not fixed to the abutments and they will therefore move independently of each other during the DCLS and CALS events. This solution will minimise the forces on the piles and therefore prevent their failure during these design events.

## Slide 19: Seismic Pipe Movement
Longitudinal movement
Transverse movement
Superstructure movement on abutments
Combinations of above
Notes: Seismic Pipe Movement
Much more deflection than previous scenarios.
Pipe restricted in transverse direction. Snaking forces.
Each end can float.
DCLS. 360mm movement. Two thirds of allowable deflection in joints. After event reset in place.
CALS. Right on limit of allowable rotation. Extensive but repairable.
This means that we need to design for one further scenario which requires far more deflection from the pipe joints than the previous 2 scenarios mentioned. One thing I have not yet mentioned is that we can not let the pipe be free in the transverse direction on the bridge because this pipe moving or snaking in the transverse direction in a seismic event will put very large loads on the superstructure which are not feasible to design for. However what we can do, is allow the pipe supports of the first length of pipe at each end to be able to float which then allows for this movement.
As mentioned on the previous slide, for an SLS event, the superstructure is not designed to move on the abutments. However for the DCLS and CALS events, the superstructure is expected to move. (CLICK)
Our modelling shows that for the DCLS event, there is expected to be 363mm of differential movement between the bridge superstructure and the abutment. This would result in a 3.92 degree rotation of the pipe joints closest to the abutment which is within the 5.83 degree limit of the pipeline. Following this level of event, it would be expected that the superstructure be reset into its original place.
For the CALS event, we would expect 5.87 degrees of rotation. This may just exceed the limit of the pipeline. However this still meets the design requirements as during a CALS event, where the damage is expected to be extensive but repairable.
Finally for combined movements, the results are very similar as the final scenario as the first two scenarios have minimal movements or deflections even during a CALS event. Also to note, the deflection each joint allows is dependent on the contraction or extension of each joint. Our design parameters have used the worst case scenarios.

## Slide 20: Construction
Notes: Construction
Tight site
Started 2022 – 3 years.
Progress – Scaling, rock anchors, southern abutment piles
Access issues – helicopter.
- Pipes stored offsite. Installed alter 2023.
For your interest, construction started near the beginning of 2022 and the programme will take approximately 3 years. So far scaling works have been undertaken and a large number of rock anchors have been installed for slope stability purposes. The southern abutment piles have been installed and the tower crane foundations are currently in the process of being constructed. This picture further demonstrates the site constraints. Unfortunately there is limited work that can be carried out at the same time due to access issues. The contractor (BPC) have even used a helicopter to transport equipment in to help speed up the programme on the northern side whilst works are being undertaken on the southern side of the river.
Our pipes have been delivered and are being stored onsite with some of the pipe installation starting later in 2023.

## Slide 21
Acknowledgements
Notes: NEED TO ADD FURTHER LOGOS AS PER THE PAPER.
I’d like to thank the following partners in this project…..