## Introduction and Instructions
WINTER WATER USE CALCULATION TEMPLATE
Version 1 2023 | INTRODUCTION
1 | The Winter Water Use Calculation Template software is an Excel Workbook that is used to (effectively) calculate a water balance over a winter period (minimum month) when customer water use is generally more certain with minimal outdoor water use and irrigation. From these calculations the level of water loss in a water supply network can typically be assessed with reasonable certainty. The calculations work best if all non-residential properties are metered and these meters are read at least four-monthly, so that non-residential water use through winter is known with some certainty. Note that rural lifestyle blocks and properties with swimming pools will ideally be included in this ‘non-residential’ category for the purposes of these calculations. The calculations also require an assessed ‘per capita residential water use’ in winter, for which 160 litres/person/day is recommended. (Note - this figure excludes leakage from private underground service pipes which is dealt with separately in the calculations). NOTE: This tool is recommended for water balance calculations where residential water use is unmetered (and some non-residential water use may also be unmetered). A 'Notional' ILI for the network will be calculated which can be considered along with 'Snapshot ILI' and other considerations when arriving at an assessed level of water loss for the network. If all customer connections are metered, then there is no need to use this tool.
2 | Cells in the Worksheets are colour-coded as shown below; all cells and blocks are protected except for the yellow Data Entry Cells.
Data entry cells
Calculated values
3 | Uncertainty Considerations- All calculations include optional sensitivity testing; if the user enters 95%ile estimates of random errors in input data, the software calculates 95%ile errors for the 'Notional ILI'. The calculations are based on the assumption that the random errors are distributed according to a Normal (Gaussian) distribution. For the calculation of the Notional ILI value, the user enters a 'best estimated' value for each input parameter. The user is then required to make a judgement as follows: 'I think the value I have entered is probably within +/- X% of the true value'. The value of X is then assumed to represent the 95% confidence limits, expressed as a % of the best estimated value.
INSTRUCTIONS
4 | With reference to a graph of daily water volume supplied into the network over 18 months or more, select a month or similar period of stable and minimum water use in a recent 'winter' period within the water balance period. Record the dates of this period in the top left data entry cell. Then enter the 'average daily volume of water supplied' during this period in m3/day.
5 | System Data - Enter the 'Average Household Occupancy', the number of unmetered non-residential connections, and the number of unmetered residential connections.
6 | Billed Metered Consumption - From the billing information, calculate the average daily volume billed over the winter/low water use period. If only annual billing data is available, assume 90% of average daily billing in winter (or some other reasonable value). Repeat this for the categories of water account billing cycles (monthly, three monthly, six-monthly etc). Enter the values in m3/day.
7 | Unmetered Non-Residential Consumption Assuming all non-residential properties with more than nominal water use are metered, it is generally reasonable to allow a figure of 650 to 750 litres/connection/day for these properties. Enter the assumed daily water use in litres/connection/day. The software multiplies this figure by the number of unmetered residential properties to established an assessed daily volume of water used by these properties, in m3/day.
8 | Unmetered Residential Consumption - There are two components covering this water use: Assessed Customer Night Consumption Enter a value to represent average water use (indoor) per residential customer. A figure of 160 litres/person/day is recommended. The software multiplies this figure by Average Household Occupancy to obtain a value in litres/connection/day. Then this figure is multiplied by the number of unmetered residential properties to established an assessed water use(indoor) for these properties, in m3/day. Assessed Leakage from Customer Underground Service Pipes (UGSP). There is a formula near the bottom of the ‘Consumption’ worksheet in the Benchloss Software for calculating an average figure for UGSP leakage, which typically calculates to around 30-40 litres/connection/day. Enter this figure into the spreadsheet. The software calculates the estimated total volume of leakage from private residential UGSPs, in m3/day.
9 | Other Water Use Other known water use over and above that above, and over and above what the default values for Unbilled Authorised Consumption and Apparent Losses allow for can be entered here, in m3/day.
10 | Allowance for Unbilled Authorised Consumption and Apparent Losses The spreadsheet calculates this allowance based on the default values in the Benchloss Manual.
11 | Balance = Estimated Real Losses The spreadsheet calculates the 'balance' of the water use (i.e. System Input Volume less all of the above components of water use) and this represents the assessed level of real water losses occurring during this part year water balance period.
12 | Unavoidable Annual Real Losses (UARL) for the network. Enter this value taken from the Benchloss Calculations for the network.
13 | Calculated Notional ILI Based on Winter Water Use The spreadsheet calculates a 'Notional ILI' for the network based on the Estimated Real Losses/UARL.
14 | The calculated 'Notional ILI Based on Winter Water Use' needs to be considered along with 'Snapshot ILI' figure(s) for the network during the water balance period, and possibly other considerations, when arriving at a final assessed level of water loss for the network.

## Winter Water Use - Original
WINTER WATER USE CALCULATIONS |  | Average Household Occupancy
For Winter of 2022 (July 2022) |  | 2.8 |  |  |  | Std Dev | SD2
Calculations for Winter Water Use | No. | litres/person/day | l/conn/day | m3/day | 95% Conf. Limits
System Input Volume |  |  |  | 52501 | 2% | 535.7245 | 287000.729
Metered Consumption - High Users |  |  |  | 4015 | 5% | 102.4235 | 10490.5671
Metered Consumption - Two or Three Monthly Accounts |  |  |  | 7038.4667 | 5% | 179.5527 | 32239.1797
Metered Consumption - 6 or 12 Monthly Accounts |  |  |  | 0 | 0% | 0 | 0
Metered Consumption - Other |  |  |  | 0 | 0% | 0 | 0
Estimated Use from Unmetered Non-Residential Properties | 2447 |  | 650 | 1590.55 | 20% | 162.301 | 26341.6212
Estimated Use from Unmetered Residential Properties* | 56154
- Winter net litres/person/day x Average Household Occupancy |  | 160 | 448 | 25156.992 | 15% | 1925.28 | 3706703.0784
- Assessed Average Customer Underground Service Pipe (UGSP) Losses |  |  | 32 | 1796.928 | 30% | 275.04 | 75647.0016
Calculated Gross per capita Residential Consumption |  | 171.4286 | 480
Any Other Water Use (Describe) |  |  |  | 0 | 50% | 0 | 0
Allowance for Unbilled Authorised Consumption and Apparent Losses |  |  |  | 536.0753 | 50% | 136.7539 | 18701.6323
Balance = Estimated Real Losses |  |  |  | 12366.988 | 32.31% | 2038.9026 | 4157123.8093
UARL |  |  |  | 2922
Calculated Notional ILI Based on Winter Water Use |  |  |  | 4.2324 | 32.31%
* Average residential water use (indoor) in winter in New Zealand is approximately 160 litres/person/day. This excludes any UGSP leakage. |  | COLOUR CODING | Data Entry Cells | Calculated Values
Use the formula in the Benchloss software near the bottom of the Consumption Worksheet to calculate average UGSP Leakage

## TEMPLATE TO USE - OVERWRITE
WINTER WATER USE CALCULATIONS |  | Average Household Occupancy
For Winter of 2022 (July 2022) |  | 2.8 |  |  |  | Std Dev | SD2
Calculations for Winter Water Use | No. | litres/person/day | l/conn/day | m3/day | 95% Conf. Limits
System Input Volume |  |  |  | 52501 | 2% | 535.7245 | 287000.729
Metered Consumption - High Users |  |  |  | 4015 | 5% | 102.4235 | 10490.5671
Metered Consumption - Two or Three Monthly Accounts |  |  |  | 7038.4667 | 5% | 179.5527 | 32239.1797
Metered Consumption - 6 or 12 Monthly Accounts |  |  |  | 0 | 0% | 0 | 0
Metered Consumption - Other |  |  |  | 0 | 0% | 0 | 0
Estimated Use from Unmetered Non-Residential Properties | 2447 |  | 650 | 1590.55 | 20% | 162.301 | 26341.6212
Estimated Use from Unmetered Residential Properties* | 56154
- Winter net litres/person/day x Average Household Occupancy |  | 160 | 448 | 25156.992 | 15% | 1925.28 | 3706703.0784
- Assessed Average Customer Underground Service Pipe (UGSP) Losses |  |  | 32 | 1796.928 | 30% | 275.04 | 75647.0016
Calculated Gross per capita Residential Consumption |  | 171.4286 | 480
Any Other Water Use (Describe) |  |  |  | 0 | 50% | 0 | 0
Allowance for Unbilled Authorised Consumption and Apparent Losses |  |  |  | 536.0753 | 50% | 136.7539 | 18701.6323
Balance = Estimated Real Losses |  |  |  | 12366.988 | 32.31% | 2038.9026 | 4157123.8093
UARL |  |  |  | 2922
Calculated Notional ILI Based on Winter Water Use |  |  |  | 4.2324 | 32.31%
* Average residential water use (indoor) in winter in New Zealand is approximately 160 litres/person/day. This excludes any UGSP leakage. |  | COLOUR CODING | Data Entry Cells | Calculated Values
Use the formula in the Benchloss software near the bottom of the Consumption Worksheet to calculate average UGSP Leakage